## Sheet1
Sl.no | Reference Clause No. | Page No | Query from bidder | Reply from TCED
1 | Section 6. Project Requirements | 280 of 429 | Smart Meters have been designed by the manufacturers uniquely to provide the desired performance. The communication module requirements vary w.r.t their operating voltage, power requirement and other features including physical dimensions and pin configurations for each type of communication technology & their make. Hence specifying a common dimension for Communication module is restrictive. The requirement of common pluggable module with a universal interface as given in the tender specifications does not allow innovation in design & manufacture of Smart Meters as it restricts/limits the efforts in cost reduction of the Meters. Also once the meters are redesigned, type tests are to be carried out in third party laboratories which are already running full.The timeline for deployment will be beyond 12 months. Request note that plugging in a different make/model of communication module does not guarantee that the Meter & module combine will meet the specification & standard and this will void the warranty of the Meter as well. In view of these multiple reasons,request remove this requirement of common dimensions/pin-out details of the communication module to ensure hassle-free rollout of the AMI solution. | As per RFP
2 | Section 6. Project Requirements |  | Request you to provide tamper logic as per utility requirements for all types of smart meters. | Will be finalised during the design stage
3 | Section 2 A1 | 21 | To strengthen the PQR requirement we should propose: - 1. Follow of SBD document (Whatever relaxations are given in the tender should be removed) 2. Meter manufacturer QR to be strengthened as: Option 1: Should have manufactured and supplied minimum [1,00,000] nos. of Smart meters (cumulative) on proposed communication technology in Indian/Global Power Distribution Utility in the last 7 (seven) years. And Option 2: Should have manufactured and supplied minimum [20,00,000] nos. of static electricity meters (cumulative) in Indian/Global Power Distribution Utility in the last 7 (seven) years. | As per RFP
4 | 31 | 55 | Advance Payment security (Optional)]- Deleted---As per specs the provision of advance payment is mentioned and in this clause the same is deleted. Kindly clarify. | No optional Advance Payment
5 | 12 | 256 | Project Implementation Schedule- In page 256 of SBD, it is mentioned that the installation milestone - Within 6 months from the date of execution of the Contract. But in Tender Notice, the Duration of the Assignment - 10 months implementation period + 110 months O&M Period. Which one to consider? | Installation of 100% meters is within 6 months and project implementation within 10 months
6 | Section6.Project Requirements | 160 | Please specify whether new service cable for Single Phase and Three Phase meters are to be supplied by AMISP or existing service cable to be reused | As per RFP BoQ
7 | Section6.Project Requirements | 160 | Please specify for DT Meter, steel structures, are to be supplied by AMISP or not, Please share the rating of DT with quantity for correct estimation of accessories like cable lugs, CT etc. | As per RFP
8 | Section 6. Project Requirements | 160 | Please specify the quantity and share the Technical Specifications of 9X1 cabinet box | AS per RFP BoQ
9 | Section 5. Bidding Forms- Financial Proposal | 153 | Please clarify whether other accessories like structure material, ACSR conductor, Pin Insulators, Control cable of CT PT set will be provided by the utility or not. Who will do the installation of these CT PT Set for the Feeder Meter | As per RFP BoQ (CT PT will be supplied and installed by TCED)
10 | Section 5. Bidding Forms- Financial Proposal | 215 | Please clarify whether the utility will provide the existing GIS database or not. Whether pole-to-pole numbering is to be carried out by AMISP or not. This will help AMISP in cost estimation. | GIS database not available
11 | Utility information |  | Please share the list of circles with the quantity mentioned, where the meters are to be installed. This will help AMISP to calculate the required manpower/store/office establishment. | As per RFP
12 | 13-Annexure A--Current Rating | 260 | In RFP two current ratings (5-30A and 10-60A) are given for Single Phase meters. Please clarify the quantity for both ratings. We understand that the 5-30A rating is sufficient. Kindly Confirm. | 5-30A for single phase meters
13 | 13-Annexure A--Plug-in Communication Module | 261 | We understand that the Plug-In module shall be field swappable/ replaceable with the same type of Communication technology and meter. Kindly Confirm. | As per RFP
14 | Annexure A---Name plate and marking | 263 | In RFP. the nameplate on the meter should be clearly visible, effectively secured against removal and indelibly/distinctly marked in accordance with relevant IS. We request you kindly accept the nameplate printing details printed on the meter top cover, in case of meter top cover is opaque. | As per RFP
15 | Meter rating | 268 | In RFP two current ratings (10-60A and 20-100A) are given for Three Phase meters. Please clarify the quantity for both ratings. We understand that a 10-60A rating is sufficient. Kindly Confirm. | As per BOQ
16 | Annexure D | 277 | Please confirm the Class of Accuracy requirement since the quantity is not specified in this document for each Class and we will offer Class 0.5S meter. | As per BOQ
17 | Annexure F Part-III | 283 | In RFP The following reference size may adhere to irrespective of single or multiple communication options provisioned on the same module. This standard form factor and dimensions will enable physical and functional interoperability with different makes of meters. it may not be feasible to Integrate / Interoperate the NIC Module of various Manufacturers unless otherwise, it shall require NEW DEVELOPMENT of every Meter Manufacturer. Therefore, we request to kindly remove this requirement and accept Manufacturers Design instead of Module Design | As per RFP
18 | Digital Input (DI) | 132 | Kindly clarify how Digital Input will be used in the field for HT Feeder and LT DT Meters. | No comments
19 | Annexure N | 299 | We will offer 75/5A and 50/5A Bar type CT & for CT ratio 100/5A -Bar & Ring Type other than then150/5A to 1000/5A Only ring type CT provided. | As per RFP
20 | GTP -49 | 266 | kindly accept the ( - ) head-type screws. which is more suitable. | As per RFP
21 | Annexure N | 301 | In RFP required Bore diameter of the CT shall not be less than 40 mm. Ring type We request you kindly reconfirm your requirement as these CTs have installed in SMC Box or transformer directly. Kindly clarify the same. | As per RFP
22 | Annexure N | 301 | In RFP required CT ratio required 50 to 1000A for DT transformers up to 1000KVA Need to be confirmed for Indoor CT ratio(which is fixed in SMC & Outdoor CT ratio(which is mounted on the transformer directly) | As per RFP
23 | Annexure O | 303 | In RFP required:-Specifications of 1-ph and 3-ph Polycarbonate Meter Box and 2:1 & 4:1 Meter Box for 1-ph Consumers We will purpose a 1:1 meter box for 1P and 3P consumer | As per RFP
24 | Annexure P | 307 | In RFP Box and CT chamber with SMC lid/shed fitted with the base by two nos. concealed brass hinges. We will offer Stainless Steel Hinges to be fitted with the Meter Box Body Base and the Cover. Stainless steel has more strength as compared to Brass and has corrosion resistance properties. Kindly confirm the acceptance | As per RFP
25 | Annexure T: Specification of Polycarbonate Seals. | 323 | Specification of Poly Carbonate Seals required for Sealing of Single / Poly Phase Meters. We request you to kindly confirm, Number of seals for each meter. | As per Meter sealing requirememt
26 | EMD related In Form-20 (Integrity Pact) | 38 & 119 | Section 5: Page 119: 1) clause no 5.2 it is mentioned that Bid security/EMD shall be valid for upto a period of 10 years. Section 3 Page no.38 2) Where as per ITB clause no 12.3 : The Bid security shall be valid for 90 days beyond the end of the validity period of bid specified in ITB 12.1 (ie. 180 days). We request you to kindly confirm/amend the EMD validity for 90 days beyond the end of the validity period as per ITB | Bid Security/EMD shall be valid for a period of 10 years
27 | EMD/ BG related | 82 | EMD/PBG can be provided from Scheduled Small finance banks, Standard Chartered Bank and EXIM Bank also. | As per RFP
28 | Payment related |  | Any Govt Subsidy/ Grant against consumer electricity consumption bill provided by State Govt, will also be part of funds available for Direct Debit for payment AMISP Service charges through direct debit mechanism | No comments
29 | General |  | The estimated Bid Value indicated above is being declared solely for the purpose of guidance on the EMD amount and for determining the Eligibility Criteria related to Turn Over, Past Performance Projects / Past Experience etc. This has no relevance or bearing on the price to be quoted by the bidders and will also not have any impact on bid participation. Also, this is not going to be used as a criterion in determining the reasonableness of quoted prices which would be determined by the buyer based on its own assessment of reasonableness and based on competitive prices received in the Bid / RA process | No comments
30 | Single Phase 5-30A/10-60A meter | Page 124 of 429 /Sr.No.38, Page 261 of 429/Annexure-A | Adaptability between NAN and WAN communication is possible through firmware up- gradation. Kindly we request to accept the same. | As per RFP
| 3 Phase 10-60A/20-100A meter | Page 128 of 429 / Sr.No.38, Page 269 of 429 / Annexure-B
31 | Single Phase 5-30A/10-60A meter | Page 259 of 429 | Kindly accept physical SIM card of any service provider alternatively. | As per RFP
| Three Phase 10-60A/20-100A meter | Page 267 of 429
| HT meter | Page 276 of 429
32 | Single Phase 5-30A /10-60A meter: Communication | Page 259 of 429 | Kindly accept the 'Plug-in communication module removal' event as per corresponding part of IS 15959. 'Plug-in communication non-responsive' event is not supported by corresponding part of IS 15959 and same may be deleted from spec. | As per RFP
| three Phase 10-60A/20-100A meter: | Page 267 of 429 LTCT Meter Page 273 of 429
| HT meter: | Page 276 of 429
33 | LTCT meter: | Page 273 of 429 / Annexure-C | Kindly note that recurring cost will be more with two SIM cards. You are requested to accept single physical SIM card of any service provider alternatively. | As per RFP
| HT meter | Page 276 of 429/ Annexure-D
| HT meter: | Page 133 & 277 of 429 | Please confirm the current rating of the meter is - /5A or -/1A. We request to accept the current rating of the meter is -/5A and accuracy of the meter is 0.5s. | As per BOQ
34 | HT meter: | Page 133 & 277 of 429 | We request to amend as the class of accuracy is 0.2s or 0.5S. | As per BOQ
35 | Clause 2.3 – HES | Page 172 of 429 | We request to accept the HES System on windows based platform. | As per RFP
36 | Clause 2.3 – HES | Page 172 of 429 | This is not practicable to read meter data with a frequency of 15 min interval meter reads. Please accept meter data reading frequency for every 4 hours alternatively. | As per RFP
37 | Clause 2.3 – HES | Page 173 of 429 | We need to manually enter the details of all the Smart Meters into HES. Profile shall be downloaded automatically at the time of schedule. HES shall store meter profile status by meter type, software versions, device IDs. Hardware version, logged in / logged out requirements are not understood, kindly we request to clarify the same. | As per RFP
38 | Clause 2.3.1 – HES – Configuration_p | Page 174 of 429 | Kindly provide the list of monitored parameters and please note that same parameter can be configured in HES only. However programmable parameters shall be in line with IS 15959 Part 2 or 3 depend on meter category. | As per RFP
39 | Clause 3.2_HES Integration with Field Devices | Page 214 of 429 | We provide HES as per relevant IS 15959 and MIOS standards. Kindly we request to accept the same. | As per RFP
40 | Annexure F | Page 280 of 429 | Kindly accept manufacturers design instead of module design mentioned here under, considering the following drawbacks with change in module design. 1. Design evaluation shall be affected. 2. Cost reduction shall be affected. 3. Product reliability shall be affected. 4. Distractive tests compatibility may affect the module. 5. BIS certification for Smart Meter shall be provided for the complete unit including the communication module. If the communication module is changed then existing BIS shall not be valid. 6. No BIS standard exists for common communication module at present. | As per RFP
41 | “Bill of Materials and Services for Smart Meters” Table Sr. No. 1.9 & 1.10 And Also Mention in BOQ | Page no. 153 | The specification of three phase CT/PT operated Smart Meter Box are not attached with technical specification . If it is required, kindly we request to provide the same. | As per RFP
42 | “Brief Scope of Work | Whereas Page no. 160 A (h) | Both mentioned requirement are contradictory we request you to please clarify whether Distribution box is in the scope of bidder or not, as the specification of Distribution box is not attached. If it is required kindly provide | As per BOQ
43 | “Brief Scope of Work” | Page no. 160 A (i) | The specification of Cabinet Box is not attached with technical specification. If it is required, kindly we request to provide the same. | As per BOQ
44 | “Inspection | Page no. 266 Sr. No. 49 | Alternatively, Slotted headless Grub/Set Screws for Terminal screws may also be accepted. Kindly confirm the acceptability of the same. | As per RFP
45 | “Annexure –N “Specifications of CT for LT-CT meters”. “TECHNICAL DETAILS” | Page no. 299 | We request to also accept the secondary leads terminals of the CT with brass Material. Kindly confirm the acceptability of the same. | As per RFP
46 | “Annexure –N “Specifications of CT for LT-CT meters”. “TECHNICAL DETAILS” | Page no. 301 | We request you to kindly accept the CT bore diameter as per manufacturer standards. Kindly confirm the acceptability for the same.. | As per RFP
47 | “Annexure –N “Specifications of CT for LT-CT meters”. “TECHNICAL DETAILS” | Page no. 301 | We request to kindly reconfirm your requirement as these CTs have installed in SMC Box or panel board. Kindly clarify the same meters”. | As per RFP
48 | GENERAL CONSTRUCTIONS” (iv) Table Sr. No. (i) | Page no. 305 | We request you to kindly accept 20 mm minimum gap between sides of the meter body and meter box. Kindly confirm the acceptability for the same. | As per RFP
49 | Annexure – P 2nd Para “Constructional Features of Meter Box” Same Clause 4th Para | Page no. 307 | As the Meter Box shall have two chambers, upper chamber to house 3 phase meter and lower chamber to house 04 nos. ring type LT CTs. So in that case, as per specification requirement of both chambers independent from each other is not safe for ingress of protection (IP). We shall provide the Meter Box with upper chamber overlapped on the lower chamber, for ingress protection of dust and water. So we request you to please delete these clauses and kindly confirm | As per RFP
50 | Annexure –P 5th Para “Constructional Features of Meter Box” | Page no. 307 | Please also accept Stainless steel hinges to be fitted with the meter Box body base and the cover. Stainless steel has more strength as compared to brass and has corrosion resistance properties. Kindly confirm the acceptance | As per RFP
51 | Annexure –P 6th Para “Constructional Features of Meter Box” | Page no. 307 | Please also accept the viewing Window in polycarbonate material having minimum thickness of 2.0 mm. Kindly confirm the acceptability of the same | As per RFP
52 | Annexure –P 1st Para “Material Of Meter Box:” On same clause 2nd Para | Page no. 308 | Both the above requirements are contradictory. Please amend the material of meter box as SMC instead of polycarbonate. Kindly confirm the same. | Both accepted
53 | Annexure –P “Rating Plate”. | Page no. 308 | Following details shall be provided as printed on metallic name plate duly riveted on meter box cover. • Name of Manufacturer • Year of manufacturing • Type of Meter • PO NO with Date • Meter Box Number • Property of UTILITY We cannot understand the requirement of the detail of ‘Type of Meter’ on the SMC box. Please explain. | As per RFP